## Settings Tabel for MRFH
Calculation Sheet for Bucket Humidifier
Chris Callahan, March 4, 2014 (chris.callahan@uvm.edu)
Source: http://blog.uvm.edu/cwcallah
Anything in blue is an input you can adjust. The main ones are outlined. Other cells are calculated and have been locked from editing.
If you run into problems with the solver routine, reference this page: http://peltiertech.com/Excel/SolverVBA.html
|  | Solving for RH when you know Tdb and Twb |  |  |  |  | Solving for Twb when you know Tdb and RH
|  | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6
Room Temp(DB) | degF | 35 | 35 | 35 | 35 | 35 | 35
Room Temp(WB) | degF | 34.24 | 34.46 | 34.78 | 34.89 | 34.95 | 26.9513
Room RH | % | 93.02% | 95.03% | 97.97% | 98.99% | 99.54% | 30%
Water Temp | degF | 100 | 100 | 100 | 100 | 100 | 100
Air Flow from Fan | CFM | 30 | 30 | 30 | 30 | 30 | 30
Bucket Diameter | inch | 12 | 12 | 12 | 12 | 12 | 12
Free Height / Air Space | inch | 3 | 3 | 3 | 3 | 3 | 3
Humid. Rate | gal/24 hr | 0.87688 | 0.87494 | 0.87212 | 0.87114 | 0.87061 | 0.93728
Calculation of Evaporation from a Water Surface
xs |  | 0.043001 | 0.043001 | 0.043001 | 0.043001 | 0.043001 | 0.043001
x |  | 0.0039612 | 0.0040474 | 0.0041734 | 0.0042168 | 0.0042406 | 0.001272
Diameter | in | 12 | 12 | 12 | 12 | 12 | 12
Free Height | in | 3 | 3 | 3 | 3 | 3 | 3
Surface Area | in2 | 113.04 | 113.04 | 113.04 | 113.04 | 113.04 | 113.04
| ft2 | 0.785 | 0.785 | 0.785 | 0.785 | 0.785 | 0.785
| m2 | 0.072966 | 0.072966 | 0.072966 | 0.072966 | 0.072966 | 0.072966
Crosssectional Flow Area | in2 | 18 | 18 | 18 | 18 | 18 | 18
CFM (Air Flow) | ft3/min | 30 | 30 | 30 | 30 | 30 | 30
Air Velocity | ft/s | 4 | 4 | 4 | 4 | 4 | 4
| m/s | 1.2195 | 1.2195 | 1.2195 | 1.2195 | 1.2195 | 1.2195
phi (Evap calculation rate) | kg/m2/h | 48.1707 | 48.1707 | 48.1707 | 48.1707 | 48.1707 | 48.1707
gh (Evaporation rate) | kg/h | 0.13722 | 0.13692 | 0.13647 | 0.13632 | 0.13624 | 0.14667
| lb/hr | 0.30325 | 0.30258 | 0.30161 | 0.30127 | 0.30108 | 0.32414
| gal/24 hr | 0.87688 | 0.87494 | 0.87212 | 0.87114 | 0.87061 | 0.93728
Air Properties (Moisture in Air, etc)
Tdb - Dry Bulb | degF | 35 | 35 | 35 | 35 | 35 | 35
| degR | 494.67 | 494.67 | 494.67 | 494.67 | 494.67 | 494.67
Twb - Wet Bulb | degF | 34.24 | 34.46 | 34.78 | 34.89 | 34.95 | 26.9513
| degR | 493.91 | 494.13 | 494.45 | 494.56 | 494.62 | 486.6213
P - Pressure | inHG | 29.921 | 29.921 | 29.921 | 29.921 | 29.921 | 29.921
| psia | 14.6958 | 14.6958 | 14.6958 | 14.6958 | 14.6958 | 14.6958
| Pa | 101324.1353 | 101324.1353 | 101324.1353 | 101324.1353 | 101324.1353 | 101324.1353
Pdb | psia | 0.099976 | 0.099976 | 0.099976 | 0.099976 | 0.099976 | 0.099976
Pwb | psia | 0.096992 | 0.097848 | 0.099104 | 0.09954 | 0.099778 | 0.072136
Ws | lb/lb | 0.0042603 | 0.0042603 | 0.0042603 | 0.0042603 | 0.0042603 | 0.0042603
W* | lb/lb | 0.0041323 | 0.004169 | 0.0042229 | 0.0042416 | 0.0042518 | 0.0030681
W | lb/lb | 0.0039612 | 0.0040474 | 0.0041734 | 0.0042168 | 0.0042406 | 0.001272
Pw | psia | 0.093002 | 0.095012 | 0.097949 | 0.098962 | 0.099515 | 0.029993
Relative Humidity (RH) |  | 93.02% | 95.03% | 97.97% | 98.99% | 99.54% | 30%
RH Error (used for solver) | [6 empty] | 0.000117%
Water temp
T | degF | 100 | 100 | 100 | 100 | 100 | 100
| degR | 559.67 | 559.67 | 559.67 | 559.67 | 559.67 | 559.67
Twb | degF | 34.24 | 34.46 | 34.78 | 34.89 | 34.95 | 26.9513
| degR | 493.91 | 494.13 | 494.45 | 494.56 | 494.62 | 486.6213
P | inHG | 29.921 | 29.921 | 29.921 | 29.921 | 29.921 | 29.921
| psia | 14.6958 | 14.6958 | 14.6958 | 14.6958 | 14.6958 | 14.6958
| Pa | 101324.1353 | 101324.1353 | 101324.1353 | 101324.1353 | 101324.1353 | 101324.1353
Pdb | psia | 0.95031 | 0.95031 | 0.95031 | 0.95031 | 0.95031 | 0.95031
Pwb | psia | 0.096992 | 0.097848 | 0.099104 | 0.09954 | 0.099778 | 0.072136
Ws | lb/lb | 0.043001 | 0.043001 | 0.043001 | 0.043001 | 0.043001 | 0.043001
W* | lb/lb | 0.0041323 | 0.004169 | 0.0042229 | 0.0042416 | 0.0042518 | 0.0030681
W | lb/lb | -0.010284 | -0.010202 | -0.010084 | -0.010043 | -0.010021 | -0.012809
Pw | psia | -0.24706 | -0.24508 | -0.24219 | -0.24119 | -0.24064 | -0.30902
RH |  | -26% | -25.79% | -25.48% | -25.38% | -25.32% | -32.52%
Solve
Note on A20: cwcallah: Mass fraction of water in air at saturation (100%RH) at water temperature.
Note on A21: cwcallah: Mass fraction of water vapor in air at current AIR conditions.
Note on A22: cwcallah: Bucket diameter
Note on A23: cwcallah: Amount of air space left above the water surface. This translates to the air flow height as it passes along the diameter of the bucket.
Note on A31: cwcallah: This is the rate of evaporation normalized by area and in SI units
Note on A33: cwcallah: This is the evaporation rate in mass or volume per unit of time.
Note on A46: cwcallah: Also Pws, saturation pressure at dry bulb temperature
Note on A47: cwcallah: Saturation pressure at wet bulb temperature
Note on A49: cwcallah: Humidity ratio at saturation. Pounds of water per pound of air when fully saturated at air conditions.
Note on A67: cwcallah: Also Pws